## POWER & KVAR 07-28-2019
POWER & REACTIVE
FEEDERS/HOUR |  | HOURS
| Power kW/kVAr | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00 | 31:00 | 32:00 | 33:00 | 34:00 | 35:00 | 36:00 | 37:00 | 38:00 | 39:00 | 40:00 | 41:00 | 42:00 | 43:00 | 44:00 | 45:00 | 46:00 | 47:00
FEEDER 1 | Active kW | 278 | 288 | 264 | 265 | 262 | 249 | 246 | 250 | 312 | 340 | 335 | 355 | 430 | 341 | 365 | 364 | 379 | 370 | 338 | 347 | 337 | 340 | 336 | 305
| REACTIVE / KVAR | 138 | 133 | 130 | 127 | 128 | 127 | 124 | 123 | 136 | 175 | 175 | 175 | 200 | 172 | 176 | 178 | 176 | 153 | 149 | 134 | 151 | 155 | 156 | 155
FEEDER 2 | Active kW | 1019 | 927 | 915 | 884 | 871 | 847 | 844 | 795 | 779 | 782 | 763 | 778 | 830 | 873 | 878 | 868 | 859 | 880 | 893 | 850 | 1062 | 1167 | 1142 | 1049
| REACTIVE / KVAR | 193 | 196 | 198 | 198 | 198 | 193 | 186 | 186 | 189 | 204 | 204 | 212 | 225 | 238 | 248 | 247 | 244 | 235 | 230 | 214 | 163 | 160 | 164 | 185
FEEDER 3 | Active kW | 1042 | 958 | 922 | 872 | 845 | 822 | 797 | 719 | 720 | 746 | 734 | 800 | 800 | 832 | 845 | 838 | 845 | 848 | 868 | 842 | 1059 | 1175 | 1174 | 1059
| REACTIVE / KVAR | 138 | 148 | 149 | 144 | 138 | 132 | 119 | 129 | 137 | 160 | 180 | 175 | 192 | 197 | 193 | 190 | 193 | 188 | 193 | 179 | 83 | 76 | 86 | 114
TOTAL GENERATION | kW | 2339 | 2173 | 2101 | 2021 | 1978 | 1918 | 1887 | 1764 | 1811 | 1868 | 1832 | 1933 | 2060 | 2046 | 2088 | 2070 | 2083 | 2098 | 2099 | 2039 | 2458 | 2682 | 2652 | 2413

## POWER & KVAR 07-23-2019
POWER & REACTIVE
FEEDERS/HOUR |  | HOURS
| Power kW/kVAr | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00 | 31:00 | 32:00 | 33:00 | 34:00 | 35:00 | 36:00 | 37:00 | 38:00 | 39:00 | 40:00 | 41:00 | 42:00 | 43:00 | 44:00 | 45:00 | 46:00 | 47:00
FEEDER 1 | Active kW | 327 | 332 | 315 | 284 | 263 | 275 | 716 | 3629 | 3969 | 3881 | 4077 | 2974 | 2566 | 4119 | 4195 | 4144 | 2750 | 1181 | 743 | 600 | 470 | 365 | 326 | 312
| REACTIVE / KVAR | 171 | 169 | 169 | 145 | 131 | 140 | 252 | 1669 | 1834 | 1822 | 1924 | 1321 | 1113 | 1926 | 1972 | 1947 | 1192 | 505 | 330 | 246 | 182 | 158 | 151 | 148
FEEDER 2 | Active kW | 946 | 890 | 855 | 840 | 821 | 832 | 799 | 697 | 785 | 874 | 898 | 925 | 987 | 1009 | 1015 | 895 | 945 | 910 | 911 | 900 | 1010 | 1043 | 979 | 884
| REACTIVE / KVAR | 192 | 192 | 194 | 192 | 187 | 177 | 177 | 188 | 199 | 238 | 263 | 289 | 318 | 299 | 290 | 253 | 288 | 269 | 257 | 185 | 147 | 145 | 166 | 182
FEEDER 3 | Active kW | 897 | 847 | 809 | 772 | 747 | 775 | 712 | 650 | 650 | 686 | 698 | 737 | 741 | 747 | 759 | 813 | 771 | 780 | 802 | 830 | 1060 | 1064 | 964 | 843
| REACTIVE / KVAR | 126 | 129 | 129 | 123 | 114 | 107 | 95 | 112 | 120 | 147 | 150 | 164 | 159 | 165 | 164 | 173 | 189 | 183 | 181 | 87 | 53 | 65 | 88 | 110
TOTAL GENERATION | kW | 2170 | 2069 | 1979 | 1896 | 1831 | 1882 | 2227 | 4976 | 5404 | 5441 | 5673 | 4636 | 4294 | 5875 | 5969 | 5852 | 4466 | 2871 | 2456 | 2330 | 2540 | 2472 | 2269 | 2039

## POWER & KVAR 01-26-25
POWER & REACTIVE
FEEDERS/HOUR |  | HOURS
| Power kW/kVAr | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00 | 31:00 | 32:00 | 33:00 | 34:00 | 35:00 | 36:00 | 37:00 | 38:00 | 39:00 | 40:00 | 41:00 | 42:00 | 43:00 | 44:00 | 45:00 | 46:00 | 47:00
FEEDER 1 | Active kW | 145 | 126 | 149 | 133 | 127 | 128 | 138 | 115 | 108 | 192 | 170 | 165 | 140 | 135 | 142 | 153 | 180 | 148 | 164 | 185 | 142 | 158 | 144 | 139
| REACTIVE / KVAR | -13 | -12 | -11 | -6 | -18 | -15 | -16 | -8 | -14 | 29 | -7 | -5 | 2 | -5 | -1 | -2 | -7 | -6 | -11 | 7 | -10 | -11 | -8 | -9
FEEDER 2 | Active kW | 897 | 851 | 807 | 803 | 790 | 785 | 797 | 785 | 761 | 776 | 812 | 835 | 890 | 885 | 885 | 901 | 883 | 922 | 1103 | 1219 | 1183 | 1183 | 1084 | 974
| REACTIVE / KVAR | 153 | 148 | 154 | 155 | 145 | 142 | 125 | 118 | 121 | 138 | 145 | 153 | 158 | 156 | 159 | 154 | 150 | 139 | 104 | 124 | 135 | 135 | 140 | 158
FEEDER 3 | Active kW | 878 | 818 | 779 | 749 | 740 | 742 | 821 | 815 | 854 | 889 | 935 | 943 | 988 | 1016 | 1015 | 1018 | 1040 | 1039 | 1256 | 1353 | 1287 | 1287 | 1139 | 991
| REACTIVE / KVAR | 118 | 119 | 116 | 114 | 99 | 100 | 82 | 89 | 103 | 121 | 134 | 132 | 150 | 189 | 179 | 145 | 144 | 128 | 83 | 84 | 90 | 90 | 106 | 117
TOTAL GENERATION | kW | 1920 | 1795 | 1735 | 1685 | 1657 | 1655 | 1756 | 1715 | 1723 | 1857 | 1917 | 1943 | 2018 | 2036 | 2042 | 2072 | 2103 | 2109 | 2523 | 2757 | 2612 | 2628 | 2367 | 2104

## POWER & KVAR 01-22-25 (2)
POWER & REACTIVE
FEEDERS/HOUR |  | HOURS
| Power kW/kVAr | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00 | 31:00 | 32:00 | 33:00 | 34:00 | 35:00 | 36:00 | 37:00 | 38:00 | 39:00 | 40:00 | 41:00 | 42:00 | 43:00 | 44:00 | 45:00 | 46:00 | 47:00
FEEDER 1 | Active kW | 150 | 164 | 138 | 142 | 137 | 161 | 252 | 1055 | 1145 | 1225 | 1244 | 408 | 650 | 1320 | 1343 | 1249 | 295 | 236 | 225 | 210 | 225 | 218 | 211 | 170
| REACTIVE / KVAR | -8 | -14 | -13 | -8 | -11 | 2 | 6 | 405 | 452 | 467 | 493 | 54 | 153 | 505 | 501 | 493 | 50 | 26 | 28 | 34 | 26 | 28 | 19 | -4
FEEDER 2 | Active kW | 925 | 864 | 839 | 818 | 797 | 815 | 839 | 737 | 715 | 729 | 771 | 811 | 814 | 826 | 851 | 892 | 872 | 858 | 1055 | 1200 | 1196 | 1167 | 1072 | 969
| REACTIVE / KVAR | 164 | 164 | 164 | 165 | 155 | 139 | 122 | 118 | 126 | 140 | 145 | 169 | 173 | 152 | 167 | 155 | 172 | 160 | 128 | 141 | 143 | 152 | 149 | 159
FEEDER 3 | Active kW | 882 | 806 | 758 | 728 | 722 | 725 | 786 | 765 | 778 | 840 | 880 | 900 | 908 | 920 | 933 | 967 | 962 | 974 | 1180 | 1305 | 1296 | 1199 | 1053 | 924
| REACTIVE / KVAR | 125 | 126 | 119 | 121 | 108 | 87 | 69 | 94 | 116 | 149 | 151 | 104 | 163 | 158 | 161 | 160 | 176 | 172 | 88 | 95 | 92 | 93 | 107 | 114
TOTAL GENERATION | kW | 1957 | 1834 | 1735 | 1688 | 1656 | 1701 | 1877 | 2557 | 2638 | 2794 | 2895 | 2119 | 2372 | 3066 | 3127 | 3108 | 2129 | 2068 | 2460 | 2715 | 2717 | 2584 | 2336 | 2063

## Total Energy Production 2024
Total Energy Production (kWh)
| January | February | March | April | May | June | July | August | September | October | November | December | Total
| 1436638 | 1240688 | 1039157 | 1454376 | 1629695 | 1766324 | 1960647 | 1924560 | 1887451 | 1876222 | 1644093 | 1612438 | 19472289

## Diesel & HFO Consump 2024
Diesel and Heavy Fuel Oil Consumption (Gallons)
| DO consumption | HFO consumption
2024-01-01 | 1694 | 93200
2024-02-01 | 21857 | 62571
2024-03-01 | 62067 | 11958
2024-04-01 | 10080 | 86655
2024-05-01 | 1321 | 106365
2024-06-01 | 5858 | 110340
2024-07-01 | 1916 | 125713
2024-08-01 | 1260 | 122441
2024-09-01 | 1330 | 121730
2024-10-01 | 9498 | 112003
2024-11-01 | 1345 | 102933
2024-12-01 | 619 | 104483
Total | 118845 | 1160392

## Power Plant Trips in 2024 (D.L)
h
Event # 1 | Date of Trip | Time of Trip | Descriptions | Breaker Closing Date | Breaker Closing Hour | Shutdown Duration
Shutdown type
|  |  | Short circuit on Feeder #2 Type 2-N, 400 amps (OCGR). |  | L1- 8:22 am L2- 9:18 am
| 4/13/2024 | 8 :13 am |  | 4/13/2024 |  | 9 min | General Outage
We had generators #2 and #3 operating and a load of approximately 2,441 kW on the system when a general outage occurred. This tripping is due to a Type 2-N, 400 amps (OCGR) short circuit on line #2. The circuit breakers of Gensets in operation during the event were tripped by the activation of the VCB’s underfrequency protection relays and those of Feeders 1 and 2 remained closed.
According to the operations department report, bird nests were discovered at Poles HW115 and PI5 during the inspection. They promptly dismantled the nests, notified back control room of the line clearing, and instructed them to put in service the feeder.
Event # 2 | Date of Trip | Time of Trip | Descriptions | Breaker Closing Date | Breaker Closing Hour | Shutdown Duration
Shutdown type
|  |  | Imbalance between the phases |  |  |  | General Outage
| 2024-06-28 | 3 :27 pm |  | 6/28/2024 | L1- 4:00 pm | 1.41 min
A general Outage was recorded in the system during the replacement of a damaged pole at the Caracol industrial park. To carry out the work, feeders 2 and 3 were put in parallel with Feeder 1 in order to deenergize the work area and continue to supply customers. During the progress of the work, an event occurred in the system which caused an imbalance between the phases and the general tripping. Note that on the GPC of Genset #1 the alarm recorded was : Negative Current Shut down.
| Date of Trip | Time of Trip | Descriptions | Breaker Closing Date | Breaker Closing Hour | Shutdown Duration
Shutdown type
Event # 3 |  |  | Underfrequency protection device activation on the Units
| 2024-07-05 | 5 :39 pm |  | 7/5/2024 | L1- 5:52 pm | 13 min | General Outage
L2- 6:33 pm
We had Genset # 1 and 2 in service and a load of around 1705 kW on the system when a general outage occurred at the power plant. This event ocurred due to the triggering of the VCBs of the generator sets by the activation of the underfrequency protection device following a Type : 2-N / OCGR / 412 amps recorded on Feeder #2.
Event # 4 |  |  | Over-current protection device activation on the Units
| 2024-07-18 | 6 :24 pm |  | 7/18/2024 | L1- 6:28 pm | 4 min | General Outage
L2- 7:02 pm
L3- 8:29 pm
We had Genset # 1 and 2 in service and a load of around 2050 kW on the system when a general outage occurred at the power plant. This event is due to the triggering of the VCBs of the Gensets by the activation of the over-current protection device following a Type : 2-N / OCGR / 632 amps recorded on Feeder #3.
According to line department inspection, the causes was found as branches of trees fell on the line at TD66, and during continuation of checks, they found out that further down at SS67, we had the same situation.
| Date of Trip | Time of Trip | Descriptions | Breaker Closing Date | Breaker Closing Hour | Shutdown Duration
Shutdown type
Event # 5 |  |  | Over-current protection device activation on Genset #1.
| 2024-08-09 | 5 :53 pm |  | 8/9/2024 | L1- 6:16 pm | 23 min | General Outage
L3- 6:06 pm
In service, Genset N°1 with a load of 1010 kW and Genset N°2 with a load of 1039 KW operating normally for a total contribution of 2,049 kW of power to the system. At 5 :53 hours a current peak occurred, causing the output of Genset N°1 due to overcurrent in stage 2, leaving only Genset N°2 in operation. The operating personnel in their immediate verification noticed a power failure on circuit No.1 and the total opening of the feeders that were energized.
Event# 6 |  |  | Over-current protection device activation on Genset #1.
| 2024-08-18 | 5 :35 pm |  | 8/18/2024 | L1- 5:39 pm | 4 min | General Outage
L2- 5:48 pm
We had Genset # 1 and 2 in service and a load of around 1660 kW on the system when a general outage occurred at the power plant. This event is due to a fault recorded on Feeder #1 which leads to the opening of Genset # 1 VCB by overcurrent, VCB of Genset # 2 and Feeder # 2 by Underfrequency 49.97 HZ.
Event # 7 | Date of Trip | Time of Trip | Descriptions | Breaker Closing Date | Breaker Closing Hour | Shutdown Duration
Shutdown type
|  |  | Overcurrent of 866 amperes Type 3-N following the entry of a rat into the Step up. |  |  |  | General Outage
| 2024-11-03 | 7 :35 pm |  | 11/3/2024 | L1- 8:40 pm | 1 :04 min
L2- 8:39 pm
L3- 8:40 pm
We had Genset # 1, 2 and 4 in service and a load of around 3128 kW in the system when occurred a general outage. This is due to an OCGR overcurrent of 866 amperes Type 3-N which occurred on the Step-up bar causing the VCB of the gensets which were in operation to trip due to overcurrent.